## S100
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Split range | CO.FC_FT101.SplitRangeON | BOOL | 0 | 0
Automatico | CO.FC_FT101.stato_pid_FC_FT101 | INT | 0 | 0
On/Off | CO.GB.bl_StatoOutput | BOOL | 1 | 0
Start pompa | CO.P101.bl_StatoOutput | BOOL | 1 | 0 | Y
Frequency | CO.P101.r_CtrlPortata_setpointPompa | REAL | EMS | 0
FlowRate | CO.FC_FT101.SP_AUTO_pid_FC_FT101 | REAL | EMS | 0
Tout | CO.GB.r_Ctrl_setpointGB | REAL | EMS | 0
Erogazione gas | CO.EV801.bl_StatoOutput | BOOL | 1 | 1
FCV101 | CO.FC_FT101.fManSyncValue_pid_FC_PT101 | REAL | 100 | 0 | Y

## S200
Name | NodeID | DATA TYPE | VALUE STANDBY | VALUE CHARGE | VALUE DISCHARGE
Charge | GVL.bl_charge | REAL | 0 | 1 | 0
Discharge | GVL.bl_discharge | BOOL | 0 | 0 | 1
Standyby | GVL.bl_standby | BOOL | 1 | 0 | 0
Automatico | CO.FC_FT201.stato_pid_FC_FT201 | INT | 0 | 1 | 1
FlowRate | CO.FC_FT201.SP_AUTO_pid_FC_FT201 | REAL | 0 | EMS | EMS
Start pompa | CO.P201.bl_StatoOutput | BOOL | 0 | 1 | 1

## S400
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Split range | CO.FC_FT401.SplitRangeON | BOOL | 0 | 0
Automatico | CO.FC_FT401.stato_pid_FC_FT401 | INT | 1 | 0
Start pompa | CO.P401.bl_StatoOutput | BOOL | 1 | 0 | Y
FlowRate | CO.FC_FT401.SP_AUTO_pid_FC_FT401 | REAL | EMS | 0
Tout | CO.EB.r_TemperOutput | REAL | EMS | 0
FV401 | CO.FV401.bl_StatoOutput | BOOL | 1 | 0 | Y
FV402 | CO.FV402.bl_StatoOutput | BOOL | 1 | 0 | Y
FV403 | CO.FV403.bl_StatoOutput | BOOL | 0 | 0
FV404 | CO.FV404.bl_StatoOutput | BOOL | 0 | 0
FV405 | CO.FV405.bl_StatoOutput | BOOL | 1 | 0 | Y
FV406 | CO.FV406.bl_StatoOutput | BOOL | 0 | 0
FCV401 | CO.FC_FT401.fManSyncValue_pid_FC_PT401 | REAL | 100 | 0 | Y

## S500
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Automatico | CO.QC_FT501.stato_pid_FC_FT501 | BOOL | 1 | 0
Abilitazione Controllo sistema primario | CO.CHP.controlloCHP | BOOL | 1 | 1
Abilitazione Controllo pompe primario | CO.CHP.attivaPompeCHP | BOOL | 1 | 1
Abilitazione Controllo potenza | CO.CHP.abilitaPotenza | BOOL | 1 | 0
Abilitazione Controllo portata pomper primario | CO.CHP.PIDpompe | BOOL | 1 | 1
Start pompa | CO.P501.bl_StatoOutput | BOOL | 1 | 0
FlowRate_Network | CO.QC_FT501.SP_AUTO_pid_FC_FT501 | REAL | EMS | 0
FlowRate_CHPloop | CO.CHP.setpointPortata | REAL | EMS | 100
Pel | CO.CHP.SetPointPotenzaHMI | REAL | EMS | 0
FV917 | CO.FV917.bl_StatoOutput | BOOL | 0 | 0
FV918 | CO.FV918.bl_StatoOutput | BOOL | 1 | 0
FV919 | CO.FV919.bl_StatoOutput | BOOL | 0 | 0
FV501 | CO.FV501.bl_StatoOutput | BOOL | 1 | 1
FV502 | CO.FV502.bl_StatoOutput | BOOL | 1 | 1

## S300
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Automatico - Pompa 301 | CO.FC_FT301.stato_pid_FC_FT301 | INT | 1 | 0
Automatico - Pompa 302 | CO.FC_FT302.stato_pid_FC_FT302 | INT | 1 | 1
Automatico - Pompa 601 | CO.FC_FT601.stato_pid_FC_FT601 | INT | 1 | 1
Automatico - Pompa 602 | CO.FC_FT602.stato_pid_FC_FT602 | INT | 1 | 1
Start pompa 301 | CO.P301.bl_StatoOutput | BOOL | 1 | 0 | Y
Start pompa 302 | CO.P302.bl_StatoOutput | BOOL | 1 | 1
Start pompa 601 | CO.P601.bl_StatoOutput | BOOL | 1 | 1
Start pompa 602 | CO.P602.bl_StatoOutput | BOOL | 1 | 1
FlowRate_301 | CO.FC_FT301.SP_AUTO_pid_FC_FT301 | REAL | EMS | 0
FlowRate_302 | CO.FC_FT302.SP_AUTO_pid_FC_FT302 | REAL | 6.5 | 6.5
FlowRate_601 | CO.FC_FT601.SP_AUTO_pid_FC_FT601 | REAL | 6.5 | 6.5
FlowRate_602 | CO.FC_FT602.SP_AUTO_pid_FC_FT602 | REAL | 6.5 | 6.5
Start HP alta temperatura KSW | CO.KSW.bl_StatoOutput | BOOL | 1 | 0
Modalità_HP_KSW | CO.KSW.bl_StatoHP | BOOL | 1 | 0
Tout_KSW | CO.KSW.SETPOINT_TEMPERATURA_Inverno | REAL | EMS | 0
Start HP bassaa temperatura XSW | CO.XSW.bl_StatoOutput | BOOL | 1 | 1
Modalità HP XSW | CO.XSW.bl_StatoHP | BOOL | 1 | 1
Tout_XSW | CO.XSW.SETPOINT_TEMPERATURA_Inverno | REAL | 45 | 45
FV922 | CO.FV922.bl_StatoOutput | BOOL | 0 | 0
FV923 | CO.FV923.bl_StatoOutput | BOOL | 1 | 0 | Y
FV924 | CO.FV924.bl_StatoOutput | BOOL | 0 | 0
FV301 | CO.FV301.bl_StatoOutput | BOOL | 1 | 0 | Y
FV302 | CO.FV302.bl_StatoOutput | BOOL | 0 | 0
FV303 | CO.FV303.bl_StatoOutput | BOOL | 0 | 0
FV304 | CO.FV304.bl_StatoOutput | BOOL | 1 | 1
FV305 | CO.FV305.bl_StatoOutput | BOOL | 1 | 1
FV306 | CO.FV306.bl_StatoOutput | BOOL | 0 | 0
FV307 | CO.FV307.bl_StatoOutput | BOOL | 1 | 1
FV308 | CO.FV308.bl_StatoOutput | BOOL | 0 | 0
FV309 | CO.FV309.bl_StatoOutput | BOOL | 0 | 0
FVA26 | CO.FVA26.bl_StatoOutput | BOOL | 0 | 0
FVA27 | CO.FVA27.bl_StatoOutput | BOOL | 0 | 0
FV601 | CO.FV601.bl_StatoOutput | BOOL | 0 | 0
FV602 | CO.FV602.bl_StatoOutput | BOOL | 0 | 0
FV403 | CO.FV403.bl_StatoOutput | BOOL | 0 | 0
FV404 | CO.FV404.bl_StatoOutput | BOOL | 0 | 0
FV603 | CO.FV603.bl_StatoOutput | BOOL | 1 | 1
FV604 | CO.FV604.bl_StatoOutput | BOOL | 1 | 1
FV605 | CO.FV605.bl_StatoOutput | BOOL | 0 | 0
FV606 | CO.FV606.bl_StatoOutput | BOOL | 0 | 0
FV607 | CO.FV607.bl_StatoOutput | BOOL | 1 | 1
FV608 | CO.FV608.bl_StatoOutput | BOOL | 1 | 1
TCV301 | CO.TCV301.r_CtrlFlow_setpointValvRegolazione | REAL | 0 | 0
TCV601 | CO.TCV601.r_CtrlFlow_setpointValvRegolazione | REAL | 100 | 0

## S900
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Start pompa | CO.P901.bl_StatoOutput | BOOL | 1 | 0
Automatico | CO.FC_FT901_PT901.stato_pid_FC_FT901 | INT | 1 | 0 |  | Aggiungere controllo di pressione su 900
FlowRate | CO.FC_FT901_PT901.SP_AUTO_pid_FC_FT901 | REAL | EMS | 0
ControlloPressione | GVL.controlloPressioneS900 | BOOL | EMS
SetpointPressione | GVL.controlloPressioneS900 | REAL | EMS
FCV901 | CO.FC_FT901_PT901.fManSyncValue_pid_FC_PT901 | REAL | 100 | 100
FV907 | CO.FV907.bl_StatoOutput | BOOL | 0 | 0
FV908 | CO.FV908.bl_StatoOutput | BOOL | 0 | 0
FV909 | CO.FV909.bl_StatoOutput | BOOL | 0 | 0
FV912 | CO.FV912.bl_StatoOutput | BOOL | 0 | 0
FV913 | CO.FV913.bl_StatoOutput | BOOL | 0 | 0
FV914 | CO.FV914.bl_StatoOutput | BOOL | 0 | 0
FV933 | CO.FV933.bl_StatoOutput | BOOL | 0 | 0
FVA02 | CO.FVA02.bl_StatoOutput | BOOL | 0 | 0
FVA03 | CO.FVA03.bl_StatoOutput | BOOL | 0 | 0
FVA06 | CO.FVA06.bl_StatoOutput | BOOL | 0 | 0
FVA09 | CO.FVA09.bl_StatoOutput | BOOL | 0 | 0
FVA10 | CO.FVA10.bl_StatoOutput | BOOL | 0 | 0
FVA12 | CO.FVA12.bl_StatoOutput | BOOL | 0 | 0
FVA13 | CO.FVA13.bl_StatoOutput | BOOL | 0 | 0
FVA16 | CO.FVA16.bl_StatoOutput | BOOL | 0 | 0
FVA19 | CO.FVA19.bl_StatoOutput | BOOL | 0 | 0
FVA20 | CO.FVA20.bl_StatoOutput | BOOL | 0 | 0
FVA23 | CO.FVA23.bl_StatoOutput | BOOL | 0 | 0
FVA26 | CO.FVA26.bl_StatoOutput | BOOL | 0 | 0
FVA30 | CO.FVA30.bl_StatoOutput | BOOL | 0 | 0
FVA32 | CO.FVA32.bl_StatoOutput | BOOL | 0 | 0
FVA33 | CO.FVA33.bl_StatoOutput | BOOL | 0 | 0
FVA35 | CO.FVA35.bl_StatoOutput | BOOL | 0 | 0
FVA36 | CO.FVA36.bl_StatoOutput | BOOL | 0 | 0
FVA39 | CO.FVA39.bl_StatoOutput | BOOL | 0 | 0
FVA42 | CO.FVA42.bl_StatoOutput | BOOL | 0 | 0
FVA43 | CO.FVA43.bl_StatoOutput | BOOL | 0 | 0

## S700_HL1
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Activate temperature control user 1 | CO.FC_HL1_FT701L.blCTRLTemperaturaRitorno | BOOL | 1 | 0
Tuser1 | CO.FC_HL1_FT701L.sp_TemperaturaRitorno | REAL | EMS | 0
FV701 | CO.FV701.bl_StatoOutput | BOOL | 0 | 0
FV702 | CO.FV702.bl_StatoOutput | BOOL | 1 | 1
Activate power control user 1 | CO.FC_HL1_FT701L.stato_pid_FC_FT701 | INT | 1 | 0
Puser1 | CO.FC_HL1_FT701L.r_PotenzaDesiderata | REAL | EMS | 0

## S700_HL2
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Activate temperature control user 2 | CO.FC_HL2_FT711L.blCTRLTemperaturaRitorno | BOOL | 1 | 0
Tuser2 | CO.FC_HL2_FT711L.sp_TemperaturaRitorno | REAL | EMS | 0
FV711 | CO.FV711.bl_StatoOutput | BOOL | 0 | 0
FV712 | CO.FV712.bl_StatoOutput | BOOL | 1 | 1
Activate power control user 2 | CO.FC_HL2_FT711L.stato_pid_FC_FT711 | INT | 1 | 0
Puser2 | CO.FC_HL2_FT711L.r_PotenzaDesiderata | REAL | EMS | 0

## S700_HL3
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Activate temperature control user 3 | CO.FC_HL3_FT721L.blCTRLTemperaturaRitorno | BOOL | 1 | 0
Tuser3 | CO.FC_HL3_FT721L.sp_TemperaturaRitorno | REAL | EMS | 0
FV721 | CO.FV721.bl_StatoOutput | BOOL | 0 | 0
FV722 | CO.FV722.bl_StatoOutput | BOOL | 1 | 1
Activate power control user 3 | CO.FC_HL3_FT721L.stato_pid_FC_FT721 | INT | 1 | 0
Puser3 | CO.FC_HL3_FT721L.r_PotenzaDesiderata | REAL | EMS | 0

## S700_HL4
Name | NodeID | DATA TYPE | VALUE ON | VALUE OFF | Delay OFF
Activate temperature control user 4 | CO.FC_HL4_FT731L.blCTRLTemperaturaRitorno | BOOL | 1 | 0
Tuser4 | CO.FC_HL4_FT731L.sp_TemperaturaRitorno | REAL | EMS | 0
FV731 | CO.FV731.bl_StatoOutput | BOOL | 0 | 0
FV732 | CO.FV732.bl_StatoOutput | BOOL | 1 | 1
Activate power control user 4 | CO.FC_HL4_FT731L.stato_pid_FC_FT731 | INT | 1 | 0
Puser4 | CO.FC_HL4_FT731L.r_PotenzaDesiderata | REAL | EMS | 0